## Sheet1
TAG | Qty | Model | Capacity | Airflow (CFM) | External Static Pressure (inH₂O) | Fluid Flow (gpm) | Fluid Type | Antifreeze (%) | Cooling | [10 empty] | Heating | [7 empty] | Electrical | [5 empty] | Water Pressure Drop Calculation
[9 empty] | EWT (°F) | LWT (°F) | EAT |  | LAT |  | Total (Btu/hr) | Sensible (Btu/hr) | Heat of Rejection (Btu/hr) | EER (Design) | EER (AHRI) | EWT (°F) | LWT (°F) | EAT | LAT | Total (Btu/hr) | Heat of Absorption (Btu/hr) | COP (Design) | COP (AHRI) | Voltage | Compressor | Fan Motor | Total Unit | MCA (A) | Max Fuse | Base Cool WPD (ft H₂O) | Motorized Valve WPD (ft H₂O) | Total Cool WPD (ft H₂O)
[11 empty] | EDB (°F) | EWB (°F) | LDB (°F) | LWB (°F) | [7 empty] | EDB (°F) | LDB (°F) | [5 empty] | RLA | FLA | FLA
WSHP-A | 1 | WSCV007 | FULL | 252 | 0.29 | 1.3 | Water | 0 | 87 | 99.1 | 75 | 63 | 59.2 | 54.5 | 6157 | 4316 | 7886 | 12.2 | 15.2 | 70 | 59.8 | 70 | 100.8 | 8425 | 6603 | 4.6 | 5 | 208-230/60/1 | 2.9 | 0.9 | 3.8 | 4.5 | 15 | 1.09 | 0.24 | 1.09
WSHP-B | 1 | WSCV009 | FULL | 300 | 0.29 | 2 | Water | 0 | 87 | 99.1 | 75 | 63 | 56.8 | 51.9 | 9319 | 5925 | 12074 | 11.5 | 13.7 | 70 | 59.8 | 70 | 110.3 | 13143 | 10177 | 4.4 | 4.4 | 208-230/60/1 | 4.3 | 0.9 | 5.2 | 6.3 | 15 | 2.17 | 0.58 | 2.17
WSHP-C | 1 | WSCV012 | FULL | 402 | 0.22 | 2.5 | Water | 0 | 87 | 99 | 75 | 63 | 56.9 | 52.9 | 11476 | 7893 | 14970 | 11.2 | 12.8 | 70 | 59.6 | 70 | 109.1 | 17090 | 12970 | 4.1 | 4.4 | 208-230/60/1 | 5.6 | 0.9 | 6.5 | 7.9 | 15 | 3.35 | 0.9 | 3.35
WSHP-D | 1 | WSCV015 | FULL | 502 | 0.1 | 2.85 | Water | 0 | 87 | 99 | 75 | 63 | 56.7 | 53.5 | 13593 | 9989 | 17121 | 13.2 | 16.6 | 70 | 59.5 | 70 | 104.8 | 18960 | 14903 | 4.7 | 5 | 208-230/60/1 | 5.5 | 2.8 | 8.3 | 9.7 | 15 | 5.52 | 1.17 | 5.52
WSHP-E | 1 | WSCV019 | FULL | 602 | 0.1 | 3.6 | Water | 0 | 87 | 99 | 75 | 63 | 57.5 | 53.1 | 16885 | 11432 | 21539 | 12.4 | 15.1 | 70 | 60.3 | 70 | 104.6 | 22620 | 17401 | 4.3 | 4.6 | 208-230/60/1 | 7.2 | 2.8 | 10 | 11.8 | 15 | 7.69 | 1.87 | 7.69
WSHP-F | 1 | WSCV024 | FULL | 800 | 0.1 | 4.4 | Water | 0 | 87 | 98.9 | 75 | 63 | 57.4 | 53.9 | 20674 | 15276 | 26197 | 12.8 | 15.2 | 70 | 59.9 | 70 | 102.2 | 27943 | 22309 | 5 | 5 | 208-230/60/1 | 10.3 | 2.8 | 13.1 | 15.7 | 25 | 5.94 | 0.79 | 5.94
WSHP-G | 1 | WSCV030 | FULL | 1001 | 0.09 | 5.3 | Water | 0 | 87 | 99 | 75 | 63 | 57.6 | 54.2 | 25072 | 18863 | 31729 | 12.9 | 15.4 | 70 | 60 | 70 | 101.1 | 33767 | 26488 | 4.6 | 4.9 | 208-230/60/1 | 11.5 | 4.1 | 15.6 | 18.5 | 25 | 12.77 | 1.15 | 12.77